Data cable, U/FTP, Category 6A, AWG23, Euroclass Cca 
CU 6502 4P 500 MHz

Data cable for structured premises cabling.
For the transmission of digital and analogue voice, video and data signals.
Suitable for all ICT network applications up to class EA applications (500 MHz) in accordance with EN 50173-1 and ISO/IEC 11801. Applicable for Power over Ethernet (PoE) / PoE+.
Electrically and mechanically improved quality Cat.6A data cable - fulfils the requirements of ISO/IEC 11801, IEC 61156-5, EN 50173-1 and prEN 50288-10-1. Good shielding effect due to individually screened pairs. Compatible with all current connecting hardware in accordance with EN 50173 and ISO/IEC 11801.

Loop resistance at 20˚ C:			150 Ω/km
Mutual capacitance:				42 pF/m
Impedance at 100 MHz:				100 Ω ± 5 Ω
Coupling attenuation 
(limit curve of critical state - IEC 61156):		> 55 db
Near end unbalance 
attenuation LCL at 1-600 MHz:			> 40 db
Delay skew:					5 ns/100m
NVP:						79%

Frequency [MHz]	1	4	10	100	250	500		
Attenuation [dB/100 m]	2,1	3,8	5,9	19	30	43			
NEXT [dB]	93	93	93	93	83	75			
PS NEXT [dB]	90	90	90	90	80	72		
ACR-N [dB]	91	89	87	73	53	32		
PS-ACR-N [dB]	88	86	84	70	50	29		
ACR-F [dB]	96	96	96	74	56	33		
PS-ACR-F [dB]	93	93	93	71	53	30			
Return loss [dB]	26	28	30	30	27	21		

Bending radius 		during draw-in:		≥ 56 mm
			permanently installed:	≥ 28 mm
Tensile strength:				≤ 95 N
Crush resistance:				≥ 1000 N/10 cm
Impact resistance:				≥ 10 impacts
Temperature range	during installation:	0° C to + 50° C
			in operation:		-20° C to + 60° C
Standards: 
Zero halogen, no corrosive gases
IEC 60754-1/-2, EN 50267-2-1/-2-2, VDE 0482-267-2-1/-2-2, AREI-RGIE Art.104-SA 
Flame propagation
IEC 60332-1/-2, EN 60332-1-2, VDE 0482-332-1-2, AREI-RGIE Art.104-F1
Smoke density
IEC 61034-1/-2, EN 61034-1/-2 , VDE 0482-1034-1/-2, AREI-RGIE Art.104-SD
Reaction to fire (Euroclasses) 
EN 13501-6:  Cca-s1,d1,a1
PoE
IEEE 802.3af
Cat./Class
Cat.6A / Class EA	

Type:			Dätwyler CU 6502 4P 

Article Number:		19145300C…

quantity:		____________ m

material:		____________ €

wage:			____________ €