Data cable, F/FTP, Category 7, AWG23, Euroclass Dca
CU 7052 4P 600 MHz

Data cable for structured premises cabling.
For the transmission of digital and analogue voice, video and data signals.
Suitable for all ICT network applications up to class F applications (600 MHz) in accordance with EN 50173-1 and ISO/IEC 11801 and for the transmission of broadband signals (such as cable TV) in accordance with IEC 15018.
Applicable for Power over Ethernet (PoE) / PoE+.

Electrically and mechanically high-quality Cat.7 data cable - exceeds the requirements of ISO/IEC 11801, IEC 61156-5, EN 50173-1 and EN 50288-4-1. 
Excellent shielding effect due to individually screened pairs and overall foil screen. 
Compatible with all current connecting hardware in accordance with EN 50173 and ISO/IEC 11801.

Loop resistance at 20˚ C:			140 Ω/km
Mutual capacitance:				42 pF/m
Impedance at 100 MHz:				100 Ω ± 5 Ω
Coupling attenuation 
(limit curve of critical state - IEC 61156):		> 85 db
Near end unbalance 
attenuation LCL at 1-600 MHz:			> 40 db
Delay skew:					12 ns/100m
NVP:						81%

Frequency [MHz]	1	4	10	100	250	500	600	862	
Attenuation [dB/100 m]	1,9	3,6	5,6	17,9	28	41	46	54			
NEXT [dB]	98	98	98	98	98	90	88	81			
PS NEXT [dB]	95	95	95	95	95	87	85	78		
ACR-N [dB]	96	94	92	80	70	56	42	27		
PS-ACR-N [dB]	93	91	89	77	67	53	39	24		
ACR-F [dB]	96	96	96	76	68	54	43	35		
PS-ACR-F [dB]	93	93	93	73	64	51	40	32			
Return loss [dB]	24	28	31	31	26	24	23	20		

Bending radius 		during draw-in:		≥ 60 mm
			permanently installed:	≥ 30 mm
Tensile strength:				≤ 110 N
Crush resistance:				≥ 1000 N/10 cm
Impact resistance:				≥ 10 impacts
Temperature range	during installation:	0° C to + 50° C
			in operation:		-20° C to + 60° C

Standards: 
Zero halogen, no corrosive gases
IEC 60754-1/-2, EN 50267-2-1/-2-2, VDE 0482-267-2-1/-2-2, AREI-RGIE Art.104-SA
Flame propagation
IEC 60332-1/-2, EN 60332-1-2, VDE 0482-332-1-2, AREI-RGIE Art.104-F1
Flame spread
IEC 60332-3-24, EN 60332-3-24, AREI-RGIE Art.104-F2
Smoke density
IEC 61034-1/-2, EN 61034-1/-2 , VDE 0482-1034-1/-2, AREI-RGIE Art.104-SD
PoE
IEEE 802.3at
Cat./Class
Cat 7 / Class F - limit values as specified by IEC 61156-6 and EN 50288-4-2 guaranteed
Reaction to Fire (Euroclass) 
EN 13501-6: Dca-s2,d1,a1

Type:			Dätwyler CU 7052 4P 

Article Number:		188514
			18851400DK

quantity:		____________ m

material:		____________ €

wage:			____________ €