Data cable, S/FTP, Category 6A, AWG23
CU 7060 4P 500 MHz

Data cable for structured premises cabling.
For the transmission of digital and analogue voice, video and data signals. Suitable for all ICT network applications up to class EA applications (500 MHz) in accordance with EN 50173-1 and ISO/IEC 11801.
Electrically and mechanically superior quality Cat.6A data cable - exceeds the requirements of ISO/IEC 11801, IEC 61156-5, EN 50173-1 and prEN 50288-10-1. Excellent shielding effect due to individually screened pairs and overall copper braid. Compatible with all current connecting hardware in accordance with EN 50173 and ISO/IEC 11801.

Loop resistance at 20˚ C:			146 Ω/km
Mutual capacitance:				42 pF/m
Impedance at 100 MHz:				100 Ω ± 5 Ω
Coupling attenuation 
(limit curve of critical state - IEC 61156):		> 75 db
Near end unbalance 
attenuation LCL at 1-600 MHz:			> 40 db
Delay skew:					4 ns/100m
NVP:						80%
Frequency [MHz]	1	4	10	100	250	500	600		
Attenuation [dB/100 m]	2,1	3,8	5,9	19,8	30	43	47			
NEXT [dB]	93	93	93	93	82	77	75				
PS NEXT [dB]	90	90	90	90	79	74	72		
ACR-N [dB]	91	89	87	73	52	34	28		
PS-ACR-N [dB]	88	86	84	70	49	31	25		
ACR-F [dB]	96	96	96	74	61	43	39		
PS-ACR-F [dB]	93	93	93	71	58	40	36			
Return loss [dB]	26	28	30	30	27	25	24		

Bending radius 		during draw-in:		≥ 65 mm
			permanently installed:	≥ 30 mm
Tensile strength:				≤ 95 N
Crush resistance:				≤ 1000 N/10 cm
Impact resistance:				≤ 10 impacts
Temperature range	during installation:	0° C to + 50° C
			in operation:		-20° C to + 60° C
Standards: 
Zero halogen, no corrosive gases
IEC 60754-1/-2, EN 50267-2-1/-2-2, VDE 0482-267-2-1/-2-2, AREI-RGIE Art.104-SA 
Flame propagation
IEC 60332-1/-2, EN 60332-1-2, VDE 0482-332-1-2, AREI-RGIE Art.104-F1
Flame spread
IEC 60332-3-24, EN 60332-3-24, AREI-RGIE Art.104-F2
Smoke density
IEC 61034-1/-2, EN 61034-1/-2 , VDE 0482-1034-1/-2, AREI-RGIE Art.104-SD
Reaction to fire (Euroclasses) 
EN 13501-6:  Cca-s1,d1,a1
PoE	IEEE 802.3at
Cat./Class
Cat 6A / Class EA - limit values as specified by IEC 61156-5 and EN 50288-10-1 guaranteed	

Type:			Dätwyler CU 7060 4P 

Article Number:		18292400CK

quantity:		____________ m

material:		____________ €

wage:			____________ €